- FORCED DRAFT CLOSED CIRCUIT COOLER

  - General

Furnish and install factory assembled closed circuit cooler of blow through, counterflow design with a horizontal single air side entry and a vertical air discharge. The unit shall be completely factory assembled and be conform to the specifications and schedules

The total fan power should not exceed … kW the total overall unit dimensions should not exceed the following :

Length: _____ mm

Width: _____ mm

Height: _____ mm

The unit will be delivered in two parts: the bottom section (pan-fan) and the middle section (heat transfer - wet coil and spray system).

The unit (top, middle and bottom section) shall be joined together with elastic sealer and bolted together with corrosion resistance fasteners.

Approved manufacturer Evapco – model LSWA________

  - Thermal Performance – Performance Warranty

The closed circuit cooler shall be capable of performing the thermal duties as shown in the schedule and on drawings and its design, thermal rating shall be guaranteed by the manufacturer.

  - Applicable Standards

- Directive 2006/42/EC on Machinery

- Directive 2014/30/EC Electromagnetic Compatibility

- CTI STD 201 Standard for Thermal Performance Certification of Evaporative Heat Rejection Equipment.

- Eurovent Certification operation manual OM-4-2016 CT and Rating Standard RS 9C 001 for Cooling Towers.

- Directive 2014/68/EU Pressure Equipment Directive

  - Submittals

- The manufacturer shall submit a five year history of the proposed type of closed circuit cooler with a   minimum of 10 installations for similar sized equipment.

- Shop drawings: submit shop drawings indicating dimensions, weight loadings and required clearances.

- Product data: submit manufacturer’s technical product data, original selection printouts and clearance requirements.

- Complete noise data sheet for the selected closed circuit cooler.

- Maintenance data for the closed circuit cooler and accessories.

- The closed circuit cooler manufacturer shall provide factory test run certificates of the fans and fan motor.

  - Product Delivery – Storage and Handling

- The contractor shall make the provisions for proper storage at site before installation and handle the product per the instructions of the manufacturer.

- Once installed provide the necessary measures that the units remain clean and protected from any dust and mechanical damage.

  - Quality Assurance

- The manufacturer shall have a quality assurance system in place which is certified by an accredited registrar and complying with the requirements of ISO 9001:2008. This is to guarantee a consistent level of product and service quality.

- Manufacturers without ISO 9001:2008 certification are not acceptable.

  - Warranty

- The products will be warranted for a period of minimum two years from the date of shipment.

- PRODUCT

  - Construction – Corrosion Resistance

- STANDARD EXECUTION – GALVANIZED STEEL Z725

- The structure and all steel elements of the pan and casing shall be constructed of Z-725 hot dip galvanized steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating are not accepted as equal.

- The strainer shall be made of stainless steel type 304L or 316L.

- During fabrication all panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non flammable construction.

- OPTIONAL EXECUTION – BASIN IN SST 304L or 316L

- The structure and all steel elements of the pan up to the water level shall be made of SST 304L or 316L.

- Alternatives with hot dip galvanized steel and epoxy coatings in lieu of the SST 304L or 316L are not considered equal and will not be accepted.

- All other steel components and the casing shall be constructed of Z-725 hot dip galvanized        steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating are not accepted as equal.

- The strainer shall be made of stainless steel type 304L or 316L.

- During fabrication all galvanized steel panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non flammable construction.

- OPTIONAL EXECUTION – COMPLETE UNIT IN STAINLESS STEEL SST 304L or 316L (except moving parts)

- The structure and all steel elements shall be made of SST 304L or 316L.

- Alternatives with hot dip galvanized steel and epoxy coatings to replace the SST 304L or 316L are not considered equal and accepted.

- Casing materials shall be of non flammable construction.

  - Pan / Fan Section

- The pan – fan section shall include fans and drives mounted and aligned in the factory. These items shall be located in the dry air stream.

- Standard pan accessories shall included circular access doors, strainer(s) of anti vortex design, brass make up valve with unsinkable, foam filled plastic float arranged for easy adjustment.

- The basin bottom shall be sloped to provide drainage of the complete basin section.

  - Mechanical Equipment

    - Fan(s)

- Fans shall be dynamically balanced forward curved centrifugal type fans.

- Fan housings shall have curved inlet rings for efficient air entry and rectangular discharge cowls which extend into the basin to increase fan efficiency and to prevent water from splashing into the fans.

- Curved inlet rings shall be made of the same material as the closed circuit cooler.

- All fans will undergo a dry running test in the factory after being installed in the closed circuit cooler basin.

- The fans will be mounted on a common shaft with forged bearing journals.

- Easy to remove fan screens shall be provided to avoid direct contact with the moving parts.

    - Bearings and Drive

- The fan shaft(s) shall be supported by heavy duty, self aligning pillow block bearings with cast iron housings and lubrication fittings for maintenance.

- The fan drives shall be V belt type with taper lock sheaves designed for 150 % of the motor nameplate horsepower.

- The bearings shall be rated for an L-10 life of 75.000 hours.

    - Motor

- The fan motor shall be Totally Enclosed, Fan Cooled (TEFC), squirrel cage, ball bearing type motor.

- The motor shall be minimum IP 55 degree of protection, Class F insulation, Service Factor 1 and selected for the appropriate closed circuit cooler duty and the correct ambient temperature but minimum 40 °C.

- Motor bearings shall be greased for life or external grease lines shall be provided.

- The motor shall be mounted on an adjustable heavy duty steel motor base.

- The motor selection shall be selected for the appropriate external static pressure.

- The motor power supply shall be …… volts, ….. Hertz and ….. Phase.

  - Casing Section

    - Latent Heat Transfer Coil

- The closed circuit cooler shall use internally enhanced heat exchange coils of an elliptical tube design to obtain lower air flow resistance and allow higher water loadings around the tubes.

- The heat transfer coil(s) shall be made of all prime surface, encased in a steel framework and hot dip galvanized after fabrication as a complete assembly.

- The tubes shall be arranged in a self spacing, staggered pattern in the direction of air flow for maximum heat transfer efficiency and minimum pressure drop.

- The heat exchange coils shall be air pressure tested under water.

- The design and manufacturing process shall be approved and in accordance with the “Pressure Equipment Directive” – PED 2014/68/EU.

- The manufacturer shall be responsible for the manufacturing and performance testing of the entire heat transfer coil. This is to assure single source responsibility.

- The casing shall totally encase the complete coil section to protect the complete coil from direct atmospheric contact.

- The pressure drop of the process fluid through the coil shall not exceed ……kPa.

OPTIONAL – Latent Heat Transfer Coil in SST 304L or 316L or 316L

- The closed circuit cooler shall use heat exchange coils of an elliptical tube design to obtain lower air flow resistance and allow higher water loadings around the tubes.

- The heat transfer coil(s) shall be made of SST 304L or 316L or 316L encased in an SST 304L or 316L or 316L framework and externally passivated after fabrication as a complete assembly.

- The tubes shall be arranged in a self spacing, staggered pattern in the direction of air flow for maximum heat transfer efficiency and minimum pressure drop.

- The heat exchange coils shall be air pressure tested under water.

- The design and manufacturing process shall be approved and in accordance with the “Pressure Equipment Directive” – PED2014/68/EU.

- The manufacturer shall be responsible for the manufacturing and performance testing of the entire heat transfer coil. This is to assure single source responsibility.

- The casing shall totally encase the complete coil section to protect the complete coil from direct atmospheric contact.

- The pressure drop of the process fluid through the coil shall not exceed ……kPa.

    - Water Distribution

- The spray header and branches shall be constructed of Schedule 40, Polyvinyl Chloride (PVC) pipe for corrosion resistance and shall have a steel connection to attach the external piping.

- The internal tower water distribution piping shall be easily removable for cleaning purposes.

- The water shall be distributed over the fill by precision molded ABS spray nozzles with large minimum 25 mm orifice openings and integral sludge ring to eliminate clogging.

- The nozzles shall be threaded into the water distribution piping to assure positive positioning.

    - Drift Eliminators

- The drift eliminators shall be constructed entirely inert polyvinyl chloride (PVC) that has been specially treated to resist ultra violet light.

- Assembled in easily handled sections, the eliminator blades shall be placed on 25 mm centers and shall incorporate three changes in air direction to assure efficient removal of entrained moisture from the discharge air stream.

- The maximum drift rate shall not exceed 0,001 % of the circulating water rate.

- The Drift Eliminators shall be certified according to Eurovent Standard OM-14-2014.

  - Sound Levels

The maximum sound pressure levels (dB) measured 15m from the closed circuit cooler operating at full fan speed shall not exceed the sound levels detailed below.

| Location | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | dB(A) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hz | Hz | Hz | Hz | Hz | Hz | Hz | Hz |  |
| Discharge |  |  |  |  |  |  |  |  |  |
| Air inlet |  |  |  |  |  |  |  |  |  |

Measurement in accordance with ISO 3744.

- ACCESSORIES (optional)

  - Electric Heaters

- The closed circuit cooler cold water basin shall be provided with an electric heater package to prevent freezing of the water in the cold water basin.

- The electric heater package includes: electric heater elements and a combination of 	thermostat and low water level cutoff.

- The heaters shall be selected to maintain 4 °C basin water temperature at …..°C ambient

- The heater(s) shall be ……V / …… phase / ….. Hz electric power supply.

  - Five Probe Electric Water Level Control Package

- The closed circuit cooler manufacturer shall provide an electric water level control package instead of the mechanical float valve arrangement.

- The package consist of the following elements :

- Multiple heavy duty stainless steel SST-316 static probes mounted in a stilling chamber outside the unit. Electrodes or sensors mounted inside the unit are not accepted as their operation will be disturbed by the moving water in the basin.

- An ABS, IP 56 case contains all the contactors for the different level probes and will provide a output signal of a relay for automatic filling and two relays for alarm levels.

- The power supply to the control package is  24 Vac / 230 Vac - ….. Hz.

- A weather protected solenoid valve for the water make up ready for piping to a water supply with pressure between 140 kPa and 340 kPa.

  - Intake Sound Attenuation

- The unit will be equipped with intake sound attenuation consisting of a hot dip galvanized                     steel housing of the same quality of the unit and completed with acoustical baffles made of                     fiberglass material which is suitable for use in closed circuit coolers.

- The intake sound attenuator is provided with large access doors which allow access to                     maintain the fans and bearings.

- The closed circuit cooler motor size must be adjusted for the additional static pressure drop          caused by the sound attenuator.

  - Discharge Sound Attenuation

- The unit will be equipped with discharge sound attenuation consisting of a hot dip galvanized steel housing of the same quality of the unit and completed with acoustical baffles made of                      fiberglass material which is suitable for use in closed circuit coolers.

- The discharge sound attenuator is provided with large access doors which allow access to 	maintain the water distribution system and the drift eliminators without removing the baffles.

- The closed circuit cooler motor size must be adjusted for the additional static pressure drop        caused by the sound attenuator.

  - Vibration switch

- A vibration limit switch shall be installed on the mechanical equipment support and wired into the control panel. The purpose of this switch is to interrupt the power to the motor in the event of excessive vibration.

- The switch shall be adjustable for sensitivity, and shall require manual reset.