- FORCED DRAFT COOLING TOWER

  - General

Furnish and install factory assembled cooling tower of forced draft counterflow design with a horizontal single side air entry and a vertical air discharge. The unit shall be completely factory assembled and conform to the specifications and schedules.

The total fan power should not exceed …. kW and the total overall unit dimensions should not exceed the following :

Length: …..mm

Width: …. mm

Height: … mm

The unit will be delivered in one part.

Approved manufacturer: Evapco – model LPT ……….

  - Thermal Performance – Performance Warranty

The tower shall be capable of performing the thermal duties as shown in the schedule and on the drawings, and its design thermal rating shall be certified by the Cooling Technology Institute (C.T.I.) and the Eurovent Certification Company (ECC).

Only models with performance certified by ECC and CTI will be approved.

Manufacturer’s performance guarantee without ECC-CTI certification for the proposed model or an independent field performance test shall not be accepted.

  - Applicable Standards

- Directive 2006/42/EC on Machinery

- Directive 2014/30/EC Electromagnetic Compatibility

- CTI STD 201 Standard for Thermal Performance Certification of Evaporative Heat Rejection Equipment.

- Eurovent Certification operation manual OM-4-2016 CT and Rating Standard RS 9C 001 for Cooling Towers.

  - Submittals

- The manufacturer shall submit a five year history of the proposed type of cooling tower with a minimum of 10 installations for similar sized equipment.

- Shop drawings: submit shop drawings indicating dimensions, weight loadings and required clearances.

- Product data: submit manufacturer’s technical product data, original selection printouts and clearance requirements.

- Performance data: submit curves showing certified and guaranteed cooling tower performance with variation in outdoor air wet bulb temperature at design air flow and design flow rate.

In addition submit performance curves for 90 % and 110 % of design water flow rate, indicating the cooling tower temperatures versus the ambient air wet bulb temperatures.

- Complete noise data sheet for the selected cooling tower.

- Maintenance data for the cooling tower and accessories.

- The cooling tower manufacturer shall provide factory test run certificates of the fans and fan motor.

  - Product Delivery – Storage and Handling

- The contractor shall make the provisions for proper storage at site before installation and handle the product per the instructions of the manufacturer.

- Once installed provide the necessary measures that the units remain clean and protected from any dust and mechanical damage.

  - Quality Assurance

- The manufacturer shall have a quality assurance system in place which is certified by an accredited registrar and complying with the requirements of ISO 9001:2008. This is to guarantee a consistant level of product and service quality.

- Manufacturers without ISO 9001:2008 certification are not acceptable.

  - Warranty

- The products will be warranted for two years from the date of shipment.

- PRODUCT

  - Construction – Corrosion Resistance

- STANDARD EXECUTION – GALVANIZED STEEL Z725

- The structure and all steel elements of the pan and casing shall be constructed of Z-725 hot dip galvanized steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating are not accepted as equal.

- The strainer shall be made of stainless steel type 304L.

- During fabrication all panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non flammable construction.

- OPTIONAL EXECUTION – BASIN IN SST 304L

- The structure and all steel elements of the Basin and Louver section up to the water level shall be made of SST 304L.

- Alternatives with hot dip galvanized steel and epoxy coatings in lieu of the SST 304L are not considered to be equal and are not accepted.

- All other steel components of the casing shall be constructed of Z-725 hot dip galvanized steel for long life and durability. Alternatives with lower zinc layer thickness and external paint or coating are not accepted as equal.

- The strainer shall be made of stainless steel type 304L.

- During fabrication all galvanized steel panel edges shall be coated with a 95 % pure zinc compound.

- Casing materials shall be of non flammable construction.

- OPTIONAL EXECUTION – Complete Unit SST 304L (except moving parts)

- The structure and all steel elements shall be made of SST 304L.

- Alternatives with hot dip galvanized steel and epoxy coatings in lieu of the SST 304L are not considered equal and accepted.

- Casing materials shall be of non flammable construction.

  - Construction – Seismic and wind load resistance

- The structural design must be designed in accordance with IBC2015 with and Importance factor (Ip) of ____, a seismic factor (SDS) up to ____g a wind load up to ____kN/m²

  - Pan/Fan Section

- The pan – fan section shall include fans and drives mounted and aligned in the factory. These items shall be located in the dry air stream.

- Standard pan accessories shall include circular access doors, strainer(s) of anti vortex design, brass make up valve with unsinkable, foam filled plastic float arranged for easy adjustment.

- The basin bottom shall be sloped to provide drainage of the complete basin section.

  - Mechanical Equipment

    - Fan(s)

- Fans shall be dynamically balanced forward curved centrifugal type.

- Fan housings shall have curved inlet rings for efficient air entry and rectangular discharge cowls which extend into the basin to increase fan efficiency and to prevent water from splashing into the fans.

- Curved inlet rings shall be made of the same material as the cooling tower.

- All fans will undergo a dry running test in the factory after being installed in the cooling tower basin.

- The fans will be mounted on either a solid or a hollow shaft with forged bearing journals.

- Easy to remove fan screens shall be provided to avoid direct contact with the moving parts.

    - Bearings and Drive

- The fan shaft(s) shall be supported by heavy duty, self aligning pillow block bearings with cast iron housings and lubrication fittings for maintenance.

- The fan drives shall be V belt type with taper lock sheaves designed for 150 % of the motor nameplate horsepower.

- The bearings shall be rated for an L-10 life of 75.000 hours.

    - Motor

- The fan motor shall be Totally Enclosed, Fan Cooled (TEFC), squirrel cage, ball bearing type motor.

- The motor shall be minimum IP 55 degree of protection, Class F insulation, Service Factor 1 and selected for the appropriate cooling tower duty and the correct ambient temperature but minimum 40 °C.

- Motor bearings shall be greased for life or external grease lines shall be provided.

- The motor shall be mounted on an adjustable heavy duty steel motor base.

- The motor selection shall be selected for the appropriate external static pressure.

- The motor power supply shall be …… volts, ….. Hertz and ….. Phase.

  - Casing Section

    - Heat transfer

- The cooling tower fill shall be PVC (Polyvinyl Chloride) of cross fluted design for optimum heat transfer and efficiency.

- The cross fluted sheets shall be bonded together for maximum strength and durability. Fill packs which are not bonded are not allowed.

- The PVC fill shall be self extinguishing for fire resistance with a flame spread rating of 5 per    ASTM E 84 – 81a.

- The fill shall be resistant to rot, decay or biological attack.

- The fill shall be able to withstand a water temperature of 55 °C. The fill sheets will be bonded together in such a way that the structural integrity of the fill makes the fill useable as a working platform.

- The cooling tower manufacturer shall be responsible for the manufacturing and performance testing of the fill. This is to assure single source responsibility.

    - Water Distribution

- The spray header and branches shall be constructed of Schedule 40, Polyvinyl Chloride (PVC) pipe for corrosion resistance and shall have a steel connection to attach the external piping.

- The internal tower water distribution piping shall be easily removable for cleaning purposes.

- The water shall be distributed over the fill by precision molded ABS spray nozzles with large minimum 25 mm orifice openings and integral sludge ring to eliminate clogging.

- The nozzles shall be threaded into the water distribution piping to assure positive positioning.

- Each cell shall have only one hot water return inlet, otherwise the cooling tower manufacturer shall provide the necessary extra provisions (piping, balancing, valves, …) to achieve the same at no extra cost.

    - Drift Eliminators

- The drift eliminators shall be constructed entirely inert polyvinyl chloride (PVC) that has been specially treated to resist ultra violet light.

- Assembled in easily handled sections, the eliminator blades shall be placed on 25 mm centers and shall incorporate three changes in air direction to assure efficient removal of entrained moisture from the discharge air stream.

- The maximum drift rate shall not exceed 0,001 % of the circulating water rate.

- The Drift Eliminators’ performance shall be certified according to Eurovent Standard OM-14-2014.

  - Sound Levels

The maximum sound pressure levels (dB) measured 15m from the cooling tower operating at full fan speed shall not exceed the sound levels detailed below.

| Location | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000 | dB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hz | Hz | Hz | Hz | Hz | Hz | Hz | Hz | Hz |
| Discharge |  |  |  |  |  |  |  |  |  |
| Air inlet |  |  |  |  |  |  |  |  |  |

Measurement in accordance with ISO 3744.

- 3.	ACCESSORIES (optional)

  - Electrical Heaters

- The cooling tower cold water basin shall be provided with an electric heater package to prevent freezing of the water in the cold water basin.

- The electric heater package includes : electric heater elements and a combination of thermostat and low water level cutoff.

- The heaters shall be selected to maintain 4 °C basin water temperature at …..°C ambient

- The heater(s) shall be ……V / …… phase / ….. Hz electric power supply.

  - Five Probe Electric Water Level Control Package

- The cooling tower manufacturer shall provide an electric water level control package instead of the mechanical float valve arrangement.

- The package consist of the following elements :

- Multiple heavy duty stainless steel SST 316 static probes mounted in a stilling tube outside the unit. Electrodes or sensors mounted inside the unit are not accepted because the functionality will be disturbed by the moving water in the basin.

- An ABS, IP 56 case contains all the contactors for the different level probes and will provide an output signal of a relay for automatic filling and two relays for alarm levels.

- The power supply to the control package is 24 Vac / 230 Vac - ….. Hz.

- A weather protected solenoid valve (PN16) for the water make up ready for piping to a water supply with pressure between 140 kPa and 340 kPa.

  - Intake Sound Attenuation

- The unit will be equipped with intake sound attenuation consisting of a hot dip galvanized steel housing of the same quality of the unit and completed with acoustical baffles made of fiberglass material which is suitable for use in cooling towers.

- The intake sound attenuator is provided with large access doors which allow access to maintain the fans and bearings.

- The cooling tower motor size must be adjusted for the additional static pressure drop caused by the sound attenuator.

  - Discharge Sound Attenuation

- The unit will be equipped with discharge sound attenuation consisting of a hot dip galvanized steel housing of the same quality of the unit and completed with acoustical baffles made of                      fiberglass material which is suitable for use in cooling towers.

- The discharge sound attenuator is provided with large access doors which allow access to maintain the water distribution system and the drift eliminators without removing the baffles.

- The cooling tower motor size must be adjusted for the additional static pressure drop caused by the sound attenuator.

  - Vibration switch

- A vibration limit switch shall be installed on the mechanical equipment support and wired into the control panel. The purpose of this switch is to interrupt the power to the motor in the event of excessive vibration.

- The switch shall be adjustable for sensitivity, and shall require manual reset.